1 channel rs485 commamd

Default state : Slave ID is 1 MODBUS command

AT command (ASCII characters)

Note:

1 In the AT command mode slave ID is invalid

2 AT commands must be uppercase, lowercase invalid

3 Jumper switch status: M0's two pads are soldered together, M1 M2 is random, as shown

9600 Band ,8 Data bits,None Parity,1 Stop Bit

Read Status:

Channel 1: AT+R1

Open :

Channel 1 : AT+O1

Close:

Channel 1 : AT+C1

Toggle (Self-locking)

Channel 1 Open : AT+T1

Latch (Inter-locking)

Channel 1 Open : AT+L1

Channel 2 Close : AT+L2

Momentary (Non-locking)

Channel 1: AT+M1

Delay

Channel 1: AT+D1=XXXX

XXXX refers to the 0000 to 9999 figures, Unit is seconds

Return command : Open1, Close1

Example 1:

Send command "AT+D1=0010", Channel 1 is "Open", after delay of 10 seconds, channel 1 is "Close"

Example 2:

Send command "AT+L1", Channel 1 is "Open", other Channels is "Close"

MODBUS command (function code 06 is Control command,03 is Read status command)

Note :

1 MODBUS command must be HEX

2 Slave ID (device address) must be consistent with the DIP switches (A0-A4)

3 Jumper switch status: M0's two pads must be disconnected, M1 M2 is random, as shown

9600 Band ,8 Data bits,None Parity,1 Stop Bit。

MODBUS 06 Command (Control command ,HEX):

| Bytes Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MODBUS Definitions | Slave ID | Function | Address |  | Data |  | CRC Check |  |
| Function | Device Address | Function | Channel number |  | Command | Delay time | CRC Check |  |
| Open | 0x00-0XF7 | 0x06 | 0x0001 |  | 0x01 | 0x00 | 2Bytes CRC |  |
| Close | 0x00-0XF7 | 0x06 | 0x0001 |  | 0x02 | 0x00 | 2Bytes CRC |  |
| Toggle (Self-locking) | 0x00-0XF7 | 0x06 | 0x0001 |  | 0x03 | 0x00 | 2Bytes CRC |  |
| Latch Inter-locking) | 0x00-0XF7 | 0x06 | 0x0001 |  | 0x04 | 0x00 | 2Bytes CRC |  |
| Momentary (Non-locking) | 0x00-0XF7 | 0x06 | 0x0001 |  | 0x05 | 0x00 | 2Bytes CRC |  |
| Delay | 0x00-0XF7 | 0x06 | 0x0001 |  | 0x06 | 0x00-0xff | 2Bytes CRC |  |

Remarks:

1 Momentary mode, delay time is 0.5 seconds

2 Delay mode, delay time is 0-255 seconds

Return command：

Command is active, return to send commands; instruction is invalid no return.

MODBUS 03 Command (Read status command ,HEX):

| Bytes Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MODBUS Definitions | Slave ID | Function | Address |  | Data |  | CRC Check |  |
| Function | Device Address | Function | Starting register address |  | Register length |  | CRC Check |  |
| Read Channel 1 State | 0x00-0XF7 | 0x03 | 0x0001 |  | 0x0001 |  |  |  |

Read status command returns (function code 03, HEX format):

| Bytes length | 1 | 1 | 1 |  | 2 |
| --- | --- | --- | --- | --- | --- |
| MODBUS Definitions | Slave ID | Function | data length | data | CRC16 Check |
| Function | Device Address | Function | data length | Relay state 0x0001 open 0x0000 close | CRC16 Check |
| Channel 1 open | 0x00-0x1F | 0x03 | 0x02 | 0x0001 |  |
| Channel 1 close | 0x00-0x1F | 0x03 | 0x02 | 0x0000 |  |

MODBUS commands you can use "Modbus Poll" input, as shown below

（CRC check generated automatically）

You can also use HyperTerminal serial input, as shown below

（Manually add CRC check）

Examples (Default state : Slave ID is 1)

Channel 1 Open ：01 06 00 01 01 00 D9 9A

Channel 1 Close ：01 06 00 01 02 00 D9 6A

Channel 1 Toggle：01 06 00 01 03 00 D8 FA

Channel 1 Latch：01 06 00 01 04 00 DA CA

Channel 1 Momentary: 01 06 00 01 05 00 DB 5A

Channel 1 Delay 10 seconds : 01 06 00 01 06 0A 5B AD

Channel 1 Delay 100 seconds: 01 06 00 01 06 64 DA 41

Read state (assuming that the channel 1 is open,).

Read channel 1 state ：01 03 00 01 00 01 D5 CA

Return open：01 03 02 00 01 79 84

Set Slave ID(Device Address)

- Read Slave ID

Send data

| Slave ID (Broadcast address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| Slave ID ( Broadcast address ) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

Broadcast address 0xff

Function code 0x03

Register address：0x00FF

Read number：0x0001

For example:

send data：FF 03 00 FF 00 01 A1 E4

Returns data：FF 03 02 00 01 50 50

FF Broadcast address，03 Function，02 length，01 is the current module Slave ID, 50 50 crc16

Note: When using this command, only one temperature module can be connected to the RS485 bus, more than one will be wrong!

- Write Slave ID

Send data

| Slave ID ( Device Address ) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| Slave ID ( Device Address ) (1) | Function (1) | Register address (1) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x06

Register address：0x00FF

Setting Content：2Bytes(1-247)

For example, The current Slave ID is 1, We need to change the Slave ID to 3:

Send data(Slave ID is 1)：01 06 00 FF 00 03 F9 FB

Returns data：01 06 00 FF 00 03 F9 FB